# Initial Kitchen Equipment Inspection Form

Baseline asset survey and preventive maintenance readiness

| Form code | PAYA F 01 | Revision | 1.0 |
| --- | --- | --- | --- |
| Restaurant or hotel |  | Site ID |  |
| Address |  | Visit date and time |  |
| Technician |  | Customer representative |  |
| Work order |  | Next due date |  |

Use this form for the first technical survey of a restaurant, hotel or commercial kitchen. Complete the asset register, applicable inspection modules, findings and evidence review. The preventive plan starts only after the baseline is reviewed and accepted.

# Status and action rules

| Result | Use |
| --- | --- |
| OK | Acceptable at time of inspection. |
| Attention | Serviceable, but maintenance or monitoring is required. |
| Critical | Unsafe, failed, leaking, unable to hold temperature, or likely to cause significant interruption. |
| N A | Equipment or check is not applicable at this site. |
| Not verified | Could not be safely or reliably checked; state the reason and required follow-up. |

Critical findings: make safe within competence, isolate and label when necessary, notify the customer immediately, create a finding, and attach evidence. Do not reset, bypass or certify protective devices outside the technician’s authorisation.

# Customer priorities and operating context

| Prompt | Response |
| --- | --- |
| Opening hours and peak periods |  |
| Available shutdown window |  |
| Top three recurring failures |  |
| Equipment causing most downtime |  |
| Existing maintenance providers |  |
| Access or permit restrictions |  |
| Special food safety or allergen constraints |  |

# Kitchen equipment asset register

Assign one PAYA asset ID and QR label per maintainable asset. Add continuation sheets when required.

| No | Asset ID | Equipment and location | Make model serial | Supply | Criticality | Condition |
| --- | --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |  |
| 2 |  |  |  |  |  |  |
| 3 |  |  |  |  |  |  |
| 4 |  |  |  |  |  |  |
| 5 |  |  |  |  |  |  |
| 6 |  |  |  |  |  |  |
| 7 |  |  |  |  |  |  |
| 8 |  |  |  |  |  |  |
| 9 |  |  |  |  |  |  |
| 10 |  |  |  |  |  |  |
| 11 |  |  |  |  |  |  |
| 12 |  |  |  |  |  |  |
| 13 |  |  |  |  |  |  |
| 14 |  |  |  |  |  |  |
| 15 |  |  |  |  |  |  |

# Expected equipment coverage

| Category | Typical assets |
| --- | --- |
| Cold storage | Walk in cold room; reach in refrigerator or freezer; undercounter; prep counter; display cabinet; bottle cooler; blast chiller or freezer |
| Ice equipment | Ice maker; ice storage bin; ice crusher or dispenser |
| Cooking | Range; oven; combi oven; pizza or deck oven; fryer; griddle; charbroiler; grill; salamander; induction; microwave; pasta cooker; steamer; kettle; tilting pan; rotisserie |
| Hot holding | Bain marie; heated cabinet; hot plate; heat lamp; proofing cabinet |
| Warewashing | Hood or conveyor dishwasher; undercounter dishwasher; glasswasher; pot washer; pre rinse spray |
| Food preparation | Mixer; planetary mixer; slicer; mincer; food processor; blender; dough roller; vacuum packer; scales |
| Beverage | Espresso machine; coffee grinder; beverage or beer dispenser; water cooler; filtration or softener |
| Extraction and air | Canopy hood; grease filters; fan and motor; duct; make up air; kitchen HVAC |
| Water and drainage | Sinks; taps; hot water heater; pumps; drains; floor gullies; grease separator |
| Utilities and safety | Electrical panels and circuits; gas isolation and detection; fire suppression; extinguishers; emergency lights; exit signs |

# Calibration and instruments

| Instrument | ID or serial | Calibration or verification due | Pre use check |
| --- | --- | --- | --- |
| Temperature probe |  |  |  |
| Clamp meter or multimeter |  |  |  |
| Airflow instrument |  |  |  |
| Other |  |  |  |

# Site operations and documents

☐ OK   ☐ Attention   ☐ Critical   ☐ N A   ☐ Not verified    Record details, measurement, photo ID or finding number for every exception.

| No | Inspection point | Result | Measurement evidence finding |
| --- | --- | --- | --- |
| 1 | Confirm contact, operating hours, peak periods, access limits and shutdown windows |  |  |
| 2 | Record utility types and isolator locations; photograph panels, gas shutoff and water shutoff |  |  |
| 3 | Collect equipment manuals, prior repair history, statutory certificates, cleaning records and warranties |  |  |
| 4 | Confirm staff-reported repeat failures, nuisance trips, leaks, temperature instability and downtime |  |  |
| 5 | Review cleaning responsibilities: operator, PAYA and specialist contractor boundaries |  |  |
| 6 | Check safe access, lighting, floor condition, ventilation and housekeeping around equipment |  |  |

## Assets and measurements

| Asset ID | Parameter | Measured | Expected or setpoint | Instrument | Photo |
| --- | --- | --- | --- | --- | --- |

# Extraction ventilation and HVAC

☐ OK   ☐ Attention   ☐ Critical   ☐ N A   ☐ Not verified    Record details, measurement, photo ID or finding number for every exception.

| No | Inspection point | Result | Measurement evidence finding |
| --- | --- | --- | --- |
| 1 | Identify hood, filter, plenum, duct, fan, motor, belt or direct drive, make up air and HVAC assets |  |  |
| 2 | Inspect filters, grease loading, corrosion, loose panels, lighting and accessible duct surfaces |  |  |
| 3 | Operate system; check unusual noise, vibration, fan rotation, overheating and weak capture |  |  |
| 4 | Observe smoke or steam capture at active appliances and signs of excessive negative pressure |  |  |
| 5 | Record access to roof or remote fan, service isolator, guard condition and last specialist duct clean |  |  |
| 6 | Inspect HVAC filters, coils, fans and condensate drain; record supply and return air temperatures |  |  |

## Assets and measurements

| Asset ID | Parameter | Measured | Expected or setpoint | Instrument | Photo |
| --- | --- | --- | --- | --- | --- |

# Electrical distribution and appliance supply

☐ OK   ☐ Attention   ☐ Critical   ☐ N A   ☐ Not verified    Record details, measurement, photo ID or finding number for every exception.

| No | Inspection point | Result | Measurement evidence finding |
| --- | --- | --- | --- |
| 1 | Record main and kitchen panel identity, supply type, ratings and circuit schedule |  |  |
| 2 | Inspect accessible panel exterior and appliance supplies for moisture, damage, heat marks, loose covers and unsafe routing |  |  |
| 3 | Confirm high load appliances have identifiable dedicated protection where required by design |  |  |
| 4 | Interview staff and function check reported combinations that cause breaker or RCD trips without defeating protection |  |  |
| 5 | Record appliance nameplate voltage, phase, current or power and plug or isolator condition |  |  |
| 6 | Electrical opening, tightening, insulation, earth continuity and RCD tests only by an authorised competent person |  |  |

## Assets and measurements

| Asset ID | Parameter | Measured | Expected or setpoint | Instrument | Photo |
| --- | --- | --- | --- | --- | --- |

# Gas system and combustion appliances

☐ OK   ☐ Attention   ☐ Critical   ☐ N A   ☐ Not verified    Record details, measurement, photo ID or finding number for every exception.

| No | Inspection point | Result | Measurement evidence finding |
| --- | --- | --- | --- |
| 1 | Identify fuel type, meter, isolation valves, emergency shutoff, interlock and gas detection where fitted |  |  |
| 2 | Inspect accessible hoses, connectors, restraints, valves and flame supervision for damage or contamination |  |  |
| 3 | Function check ignition, flame stability, burner condition and shutdown controls |  |  |
| 4 | Check extraction interlock operation where fitted; never bypass a safety interlock |  |  |
| 5 | Record combustion, pressure or tightness test certificate; specialist testing only by authorised gas personnel |  |  |
| 6 | Escalate gas smell, unstable yellow flame, failed flame supervision or damaged connection immediately |  |  |

## Assets and measurements

| Asset ID | Parameter | Measured | Expected or setpoint | Instrument | Photo |
| --- | --- | --- | --- | --- | --- |

# Refrigeration cold rooms and blast chilling

☐ OK   ☐ Attention   ☐ Critical   ☐ N A   ☐ Not verified    Record details, measurement, photo ID or finding number for every exception.

| No | Inspection point | Result | Measurement evidence finding |
| --- | --- | --- | --- |
| 1 | Create one asset record per cabinet or cold room and compare display with calibrated probe reading |  |  |
| 2 | Inspect door seals, hinges, closers, latches, insulation, lights and alarms |  |  |
| 3 | Inspect condenser cleanliness, airflow, fan noise, accessible evaporator, frost pattern and drain |  |  |
| 4 | Check for water leaks, oil staining, pipe rubbing, corrosion, damaged insulation and blocked air paths |  |  |
| 5 | Record setpoint, product or air temperature, ambient temperature and pull down or recovery observation |  |  |
| 6 | Record refrigerant type and charge from nameplate; sealed-system work only by qualified personnel |  |  |

## Assets and measurements

| Asset ID | Parameter | Measured | Expected or setpoint | Instrument | Photo |
| --- | --- | --- | --- | --- | --- |

# Ice machines and dispensers

☐ OK   ☐ Attention   ☐ Critical   ☐ N A   ☐ Not verified    Record details, measurement, photo ID or finding number for every exception.

| No | Inspection point | Result | Measurement evidence finding |
| --- | --- | --- | --- |
| 1 | Record machine, bin, filter and drain arrangement; review cleaning and sanitising history |  |  |
| 2 | Inspect water circuit and accessible food zone for scale, slime, mould, debris or damaged components |  |  |
| 3 | Check inlet, drain, air clearance, condenser cleanliness, leaks, harvest and abnormal noise |  |  |
| 4 | Inspect scoop and storage arrangements; scoop must not be stored in the ice |  |  |
| 5 | Plan cleaning and sanitising strictly to manufacturer chemical, dilution and rinse instructions |  |  |
| 6 | Record water filter or treatment type and replacement date |  |  |

## Assets and measurements

| Asset ID | Parameter | Measured | Expected or setpoint | Instrument | Photo |
| --- | --- | --- | --- | --- | --- |

# Cooking and hot holding equipment

☐ OK   ☐ Attention   ☐ Critical   ☐ N A   ☐ Not verified    Record details, measurement, photo ID or finding number for every exception.

| No | Inspection point | Result | Measurement evidence finding |
| --- | --- | --- | --- |
| 1 | Inventory every heat appliance and record energy source, rating and isolator |  |  |
| 2 | Inspect panels, feet or castors, restraints, doors, hinges, seals, knobs, handles and guards |  |  |
| 3 | Operate controls; check ignition or heating, displayed versus measured temperature and abnormal cycling |  |  |
| 4 | Test accessible operator safety functions such as door switches, high limit reset indication and emergency stop |  |  |
| 5 | Inspect for oil, grease, steam or water leaks; carbon buildup; damaged cables or hoses |  |  |
| 6 | Confirm ventilation clearance and that heat does not damage adjacent equipment or wiring |  |  |

## Assets and measurements

| Asset ID | Parameter | Measured | Expected or setpoint | Instrument | Photo |
| --- | --- | --- | --- | --- | --- |

# Warewashing

☐ OK   ☐ Attention   ☐ Critical   ☐ N A   ☐ Not verified    Record details, measurement, photo ID or finding number for every exception.

| No | Inspection point | Result | Measurement evidence finding |
| --- | --- | --- | --- |
| 1 | Record model, cycle type, chemical dosing, softener or filter and temperature display |  |  |
| 2 | Inspect door, hood, racks, wash arms, jets, strainers, tank, overflow, seals and curtains |  |  |
| 3 | Run full cycle; check fill, heat, wash pressure or spray, drain, rinse and leaks behind machine |  |  |
| 4 | Record wash and final rinse displayed temperatures or chemical sanitiser concentration as applicable |  |  |
| 5 | Inspect supply hose, drain, air gap or backflow protection and floor condition |  |  |
| 6 | Check reported shared-load breaker trips with extraction or other major loads and record evidence |  |  |

## Assets and measurements

| Asset ID | Parameter | Measured | Expected or setpoint | Instrument | Photo |
| --- | --- | --- | --- | --- | --- |

# Food preparation machinery

☐ OK   ☐ Attention   ☐ Critical   ☐ N A   ☐ Not verified    Record details, measurement, photo ID or finding number for every exception.

| No | Inspection point | Result | Measurement evidence finding |
| --- | --- | --- | --- |
| 1 | Inventory slicers, mixers, mincers, processors, blenders, vacuum packers and scales |  |  |
| 2 | Inspect plug, cable, body, feet, bowl, blade, attachment, cover, guards and labels |  |  |
| 3 | Function check start, stop, speed controls, interlocks and emergency stop where fitted |  |  |
| 4 | Check abnormal noise, vibration, overheating, leakage and movement during operation |  |  |
| 5 | Confirm removable food-contact parts are intact, cleanable and correctly fitted |  |  |
| 6 | Do not operate with a defeated guard or interlock; isolate and tag unsafe equipment |  |  |

## Assets and measurements

| Asset ID | Parameter | Measured | Expected or setpoint | Instrument | Photo |
| --- | --- | --- | --- | --- | --- |

# Beverage and water treatment

☐ OK   ☐ Attention   ☐ Critical   ☐ N A   ☐ Not verified    Record details, measurement, photo ID or finding number for every exception.

| No | Inspection point | Result | Measurement evidence finding |
| --- | --- | --- | --- |
| 1 | Inspect espresso machine, grinders, dispensers, filtration, softener and drain arrangements |  |  |
| 2 | Check leaks, hoses, fittings, cable, controls, gauges and abnormal pressure or noise |  |  |
| 3 | Record water filter and softener service dates; inspect scale condition |  |  |
| 4 | Function check brewing or dispensing, temperature, steam wand, grinder and drainage |  |  |
| 5 | Confirm cleaning or backflush routine and food-safe chemical use per manufacturer |  |  |
| 6 | Inspect CO2 cylinder restraint and regulator where beverage gas is used |  |  |

## Assets and measurements

| Asset ID | Parameter | Measured | Expected or setpoint | Instrument | Photo |
| --- | --- | --- | --- | --- | --- |

# Plumbing drainage and hot water

☐ OK   ☐ Attention   ☐ Critical   ☐ N A   ☐ Not verified    Record details, measurement, photo ID or finding number for every exception.

| No | Inspection point | Result | Measurement evidence finding |
| --- | --- | --- | --- |
| 1 | Inspect sinks, taps, pre rinse spray, supply lines, traps, floor drains, pumps and grease separator |  |  |
| 2 | Run water and observe drain speed, leaks, odour, backflow, loose taps and pooling |  |  |
| 3 | Inspect dishwasher and ice machine drain routes separately |  |  |
| 4 | Record hot water temperature at representative outlet and heater condition |  |  |
| 5 | Check grease separator access, condition, service frequency and records |  |  |
| 6 | Escalate sewage backflow, uncontrolled leak or water near electrical equipment immediately |  |  |

## Assets and measurements

| Asset ID | Parameter | Measured | Expected or setpoint | Instrument | Photo |
| --- | --- | --- | --- | --- | --- |

# Fire safety hygiene and compliance

☐ OK   ☐ Attention   ☐ Critical   ☐ N A   ☐ Not verified    Record details, measurement, photo ID or finding number for every exception.

| No | Inspection point | Result | Measurement evidence finding |
| --- | --- | --- | --- |
| 1 | Record extinguisher type, location, seal, pressure indication and service date without replacing statutory inspection |  |  |
| 2 | Inspect hood suppression system presence, nozzles, pull station, interlock and service tag |  |  |
| 3 | Function test emergency lighting or detector only when authorised and without disabling occupied-area protection |  |  |
| 4 | Check exit signs and access to isolators, exits, panels and firefighting equipment |  |  |
| 5 | Record grease, slip, sharp edge, hot surface, pest evidence and cleanability issues |  |  |
| 6 | Separate statutory compliance status from PAYA equipment condition; attach current certificates |  |  |

## Assets and measurements

| Asset ID | Parameter | Measured | Expected or setpoint | Instrument | Photo |
| --- | --- | --- | --- | --- | --- |

# Findings and corrective action register

| ID | Asset | Finding and evidence | Severity | Immediate action | Owner due |
| --- | --- | --- | --- | --- | --- |
| F-01 |  |  |  |  |  |
| F-02 |  |  |  |  |  |
| F-03 |  |  |  |  |  |
| F-04 |  |  |  |  |  |
| F-05 |  |  |  |  |  |
| F-06 |  |  |  |  |  |
| F-07 |  |  |  |  |  |
| F-08 |  |  |  |  |  |

# Preventive plan recommendation

| Asset or system | Recommended task | Frequency | Specialist or permit | Next due |
| --- | --- | --- | --- | --- |
|  |  | Monthly |  |  |
|  |  | Monthly |  |  |
|  |  | Monthly |  |  |
|  |  | Monthly |  |  |
|  |  | Monthly |  |  |
|  |  | Monthly |  |  |
|  |  | Monthly |  |  |

# Baseline review and release

| Readiness requirement | Confirmed |
| --- | --- |
| Asset IDs and locations complete | ☐ Yes ☐ No ☐ N A |
| Nameplates and baseline photos attached | ☐ Yes ☐ No ☐ N A |
| Critical findings made safe and communicated | ☐ Yes ☐ No ☐ N A |
| Measurements and instrument IDs recorded | ☐ Yes ☐ No ☐ N A |
| Specialist and statutory work identified | ☐ Yes ☐ No ☐ N A |
| Open work approved or assigned | ☐ Yes ☐ No ☐ N A |
| Monthly checklist tailored to installed assets | ☐ Yes ☐ No ☐ N A |

Baseline status:  ☐ Ready for preventive maintenance  ☐ Returned for completion  ☐ Not ready

| Technician signature |  | Date |  |
| --- | --- | --- | --- |
| Engineer reviewer |  | Date |  |
| Customer acknowledgement |  | Date |  |

# Technical boundaries and reference basis

This form is a general preventive-maintenance control document. The equipment nameplate, manufacturer manual, site risk assessment, HACCP plan and applicable Spanish or local statutory requirements take priority. Refrigerant work, gas tightness or combustion testing, live electrical testing, fire-system certification, duct cleaning and other regulated work must be performed by appropriately authorised personnel.

| Reference basis | How it is applied |
| --- | --- |
| PAYA baseline and monthly workflow | Asset identity, QR history, photo evidence, findings, engineer review and readiness gate. |
| Regulation EC 852 2004 on food hygiene | Equipment and premises must be kept clean and, where necessary, disinfected and maintained to minimise contamination risk. |
| Equipment manufacturer instructions | Cleaning chemicals, lubrication, disassembly, test limits and service intervals must follow the exact model manual. |
| Fire electrical gas and refrigeration requirements | The form records visible condition and due dates; it does not replace statutory inspection or specialist certification. |